## Slide 1
Variable Frequency Drives – Building Application & Benefits
Passion.
Enthusiasm.
Tenacity.

## Slide 2: Why is VFDs in a Building?
Energy savings
Automation
System/Simple/Sound-Control
Easy maintenance & retrofit
Bypass capability

## Slide 3: Building Loads

## Slide 4: Building Energy Analysis
Kitchens *
Others *
Lifts *
Hot Water *
Lighting *
Air Conditioning * = 60%
HVAC Load is typically 60% on commercial Installations.
50% of motors installed on fans and pumps
Majority of motors on fans / pumps are oversized.
80% speed = 50% energy.
VFDs integrated into the IOT & BMS can do so often at the lowest initial cost for the system
Variable Speed Drives (VSDs) can help reduce these costs and improve comfort levels for occupants.

## Slide 5: Flow Control
Why?
HVAC systems are designed for “best performance at the peak load/worst case” situations. Most of the time they have excess capacity.
Controlling flow
  Saves energy
  Improves occupant comfort
Methods
Air flow
  Inlet guide vanes
  Outlet dampers
  Variable pitch fan
  Variable speed
Fluid flow
  Bypass valve (three way)
  Throttling valve (two way)
  Variable speed

## Slide 6: Drive Applications
Fans
Pumps
Compressors

## Slide 7: Flow vs Speed
If the speed of the impeller is increased from N1 to N2 rpm, the flow rate will increase from Q1 to Q2 as per the given formula:

## Slide 8
Flow:
Q1 / Q2 = N1 / N2
Example: 100 / Q2 = 1750/3500
Q2 = 200 GPM
  The affinity law, the speed changed:

## Slide 9: Head Vs speed
The head developed(H) will be proportional to the square of the quantity discharged, so that
Head:
H1/H2 = (N12) / (N22)
Example: 100 /H2 = 1750 2 / 3500 2
H2 = 400 Ft

## Slide 10: Power Vs Speed
The power consumed(W) will be the product of H and Q, and, therefore
Power(kW):
kW1 / kW2 = (N13) / (N23)
Example: 5/kW2 = 17503 / 35003
kW2 = 40

## Slide 11: Fans
Supply Fan
Cooling
Heating
T
Filter
Discharge Temperature
T
Room Temperature
Air Temperature Control Panel
Outside
air
Recirculation
Exhaust
air
ROOM 1
Extraction Fan

## Slide 12: Fans

## Slide 13: Energy Balance-Pumps
ELECTRICITY
100%
12% LOSS
2% LOSS
24% LOSS
9% LOSS
11% LOSS
MOTOR
COUPLING
PUMPS
VALVES
PIPES
WORK DONE ON WATER

## Slide 14: Pumps

## Slide 15: Pumps

## Slide 16: Compressors
Condenser
Evaporator
Cooling Tower
Water
Chilled H20 Supply
Chilled H20 Return
A
P
Vane
Control
Power Control
P
4-20 mA
4-20 mA
4-20 mA
4-20 mA
4-20 mA
T
dP
T
T
ON/OFF
4-20 mA
4-20 mA
4-20 mA
Control
Panel
UNI
Notes: 5

## Slide 18: Compressors

## Slide 19: AHU Case Study

## Slide 20: Refrigeration Compressor with PM Motors
Notes: 23

## Slide 21: Energy saving Proposal for PUMP’s and AHU’s.

## Slide 22: Advantages of VFD’s
• VFDs provide the most energy efficient means of capacity control.
• VFDs have the lowest starting current of any starter type.
• VFDs reduce thermal and mechanical stresses on motors and belts.
• VFD installation is as simple as connecting the power supply to the VFD.
• VFDs provide high power factor, eliminating the need for external power factor correction capacitors.
• VFDs provide lower KVA, helping alleviate voltage sags and power outages.

## Slide 23: Total Power Consumption
Rated Motor Rating in kW | 187 | In Kw
Motor/Pump Rating in KW | 160 | in KW
Usages ( hrs/day ) | 20 | Hrs
Power Consumption ( Units/Month ) | 96000 | Units
Unit Rate | 4.5 | Rs
Power Bill / Month | 432000/- | Rs
Power Bill P. A. | 5184000/- | Rs

## Slide 24: Power Saving by putting VFD
Total Rated Motor rating in Kw | 187 | in KW
Motor/Pump Rating in KW (Eff.=85%) | 160 | in KW
Usages ( hrs/day ) | 20 | hrs
Power Consumption ( Units/Month ) | 96000 | Units
Unit Rate | 4.5 | Rs
Power Bill / Month | 432000/- | Rs
Power Bill P. A. | 5184000/- | Rs
Speed reduction | 10 | %
Power Saving | 27 | %
Power Saving P.A. | 1399680/- | Rs
VFD Price Offered | 1375000/- | Rs
Tentative pay back period | 11 | Months

## Slide 25: Tentative Payback Period
Savings/Annum by putting VFD’s= Rs 13,99,680/-
Investment for putting VFD’s = Rs 13,75,000/-
Pay Back Period for VFD’s = 11 Months.

## Slide 26: Total Savings 14 Lakh/Annum